## PKG AHU - HHW
PACKAGED AIR HANDLING UNIT SCHEDULE:
UNIT NAME | SERVING | SUPPLY AIR FAN DATA | [8 empty] | REMARKS
|  | TOTAL MAX. CFM | FAN DATA
|  |  | FAN QUANTITY | TSP IN H2O | FAN DIA. | FAN RPM | Volt/Phase/Frequency | FLA | MCA | Max fuse size
AHU 1-1 |  | 6500 cfm | 1 | 4.307 | 19.7 impeller fan full width | 2113 | 200-208/3/60 | 20.79 | 25.67 | 45.00
AHU 2-1 | SEE ERV AHU SCHEDULE
AHU 2-2 | SEE ERV AHU SCHEDULE
REMARKS:
1 | SINGLE ZONE VARIABLE VOLUME - ECM CONTROLLED
2 | MULTI-ZONE VARIABLE VOLUME - ECM CONTROLLED
3 | CONSTANT VOLUME - ECM CONTROLLED
4 | PROVIDE UNIT MOUNTED ECM ARRAY CONTROL PANEL WITH HOA AND 65K AIC/SCCR
5 | PROVIDE WALL MOUNTED FUSED DISCONNECT FOR ECM ARRAY
NOTE: THE VENTILATION RATE PROCEDURE USED FOR THIS PROJECT COMPLIES WITH ASHRAE STANDARD 62.1-2019.
OUTDOOR AIR TEMPERATURES |  |  |  | PROVIDE SEPARATE ELECTRICAL CONNECTION FOR FAN MOTORS AND ELECTRIC HEATERS
| DB | WB |  | PROVIDE DUAL POINT POWER FOR SUPPLY FAN AND INTEGRAL ELECTRIC HEATING COIL
SUMMER | 96 | 78 |  | SEE ELECTRIC DUCT HEATER SCHEDULE FOR DUCT MOUNTED COIL INFORMATION
WINTER | 34 | X |  | PROVIDE ACCESS DOORS UPSTREAM AND DOWNSTREAM OF ALL HEATING AND COOLING COILS
PROVIDE BIPOLAR IONIZATION IN THE AHU, WITH ION DETECTOR, BY CONTRACTOR NOT AHU MFR
RETURN AIR TEMPERATURES
| DB | WB
SUMMER | 78 | 67
WINTER | 70 | X